## Cover Page
Design Package
Package Contents
Tab
1 | Pad Dispersal Design Guide
2 | TDH Calculations for Selecting System Pump (1.25 inch force main)
3 | Distance to Finished Grade Calculation Sheet
4 | Kaplan Sheet (based on equations in Septic Systems Handbook)
5 | Allen Sheet (based on equations in Hydraulic Mounding of Groundwater Under Axisymmetric Recharge)
6 | Poeter Sheet (based on equations in Designing Cluster and High-Density Wastewater Soil Absorption Systems to Control Groundwater Mounding)
7 | Daily Flow Calculation per Panel Readings
©2022 Anua

## Design
Quanics Pad Dispersal Design Guide
[9 empty] | Slope % | Slope Correction Factors
Design Parameters | Design flow | 600 | gpd | AeroCell | [5 empty] | Upslope | Downslope
| Occupancy/Population Equivalent | 6 | people | BioCoir |  | A400 | 67 |  |  | 3:1 | 3:1
| Soil application rate | 0.8 | gpd/ft2 |  |  | IM1060 | 138 |  | 0 | 1 | 1
| Slope % | 2% |  |  |  | IM1530 | 250 |  | 1 | 0.97 | 1.03
| Depth to limiting layer | 36 | in |  |  | IM540 | 85 |  | 2 | 0.94 | 1.06
| Req'd separation to limiting layer | 24 | in | 2 |  | NS1000 | 137 |  | 3 | 0.915 | 1.1
| Hydraulic loading per linear foot | 6 | gpd/ft | 12 |  | NS500 | 85 |  | 4 | 0.89 | 1.14
| Dispersal option, req'd | Subsurface | [6 empty] | 5 | 0.875 | 1.18
[9 empty] | 6 | 0.85 | 1.22
Primary Compartment Sizing | Minimim (per NSF testing) | 1200 | gal, nominal | [5 empty] | 7 | 0.83 | 1.27
| State or Other req'd min | 750 | gal, nominal | Yes | DIRECTIONS: Fill-in cells highlighted GREEN, if applicable. |  |  |  | 8 | 0.81 | 1.32
| Primary compartment size, req'd | 1200 | gal, nominal | No |  |  |  |  | 9 | 0.79 | 1.37
[5 empty] | ©2022 Anua |  |  | v.240906 | 10 | 0.77 | 1.43
Dosing Compartment Sizing | Minimum (per NSF testing) | 600 | gal, nominal | A400 |  |  |  |  | 11 | 0.75 | 1.49
| State or Other req'd min | 500 | gal, nominal | IM | Mounded Pad Design | Slope ratio | 3 | :1 | 12 | 0.735 | 1.56
| Dosing compartment size, req'd | 600 | gal, nominal | NS |  | Sand rate, gpd/ft2 - Sand depth, in | 2 | 4 | 13 | 0.72 | 1.64
Note: Primary and dosing compartments may be a single, two-compartment tank | [5 empty] | Absorption area width, A | 4.5 | ft | 14 | 0.705 | 1.72
Pod Sizing | Treatment type | AeroCell |  | 4 |  | Absorption area length, B | 100 | ft | 15 | 0.69 | 1.82
| Model | A400 |  | 2 |  | Basal width, A+I or A+I+J | 7.5 | ft, min | 16 | 0.675 | 1.92
| Pods, req'd | 2 |  | 4 |  | Mound fill depth, D | 4 | in | 17 | 0.66 | 2.04
[6 empty] | Mound fill depth, E | 6 | in | 18 | 0.65 | 2.17
In-Ground Pad Design | # Pads | 1 |  | end-to-end |  | Mound depth, F | 6 | in | 19 | 0.64 | 2.33
| Pad, W | 7.5 | ft | side-to-side |  | Mound depth, G | 6 | in | 20 | 0.625 | 2.5
| Pad, L | 100 | ft | 1.6 |  | Mound depth, H | 6 | in | 21 | 0.61 | 2.7
| Pad area | 750 | ft2 | 2 |  | Downslope width, I | 4.77 | ft, calculated | 22 | 0.6 | 2.94
| Pod spacing, ft | 42.92 | end-to-end | Bottom |  | Upslope width, J | 3.76 | ft, calculated | 23 | 0.59 | 3.23
|  |  |  | Sidewall |  | Endslope length, K | 4.25 | ft | 24 | 0.58 | 3.57
Gravel Trench Design | Use bottom or sidewall area? | Bottom |  | Both |  | Total width, W | 13.03 | ft | 25 | 0.57 | 4
| Trench, W and H, in | 24 | 12 | 2 |  | Total length, L | 108.5 | ft
| # Trenches | 4 |  | 2 |  | Pod spacing, M | 42.92 | ft, end-to-end
| Trench, L | 100 | ft, per trench | 4 |  | Total mounded pad area | 1413.755 | ft2 | Slope Multiplier Look-up
| Bottom area | 750 | ft2 | 55.92% | 1.7783 | 4.77 | 1.243 | 3.76 | Slope CF | Upslope | Downslope
|  |  |  | 44.08% | Notes |  |  |  | 2% | 0.94 | 1.06
Chamber or Geosynthetic Aggregate Design | Use bottom or sidewall area? | Bottom |  | 3
| W and H, in | 36 | 7 | 1.1667
| L, in and # units per trench | 120 | 5 | 10
| # Trenches | 3 |  | 4.1667
| Trench, L | 100 | ft, per trench
| Bottom area | 750 | ft2 | 4.77
| Units, req'd | 150 |  | 4.77
| Chamber or bundle model | EZflow 0705H-GEO |  | 3.76
Mounded Pad Diagram
NOTES: | 1. NOT TO SCALE | 2. MODULE DIMENSIONS: 7.08' L x 4.58' W x 2.5' H |  |  |  | 3. DIMENSIONS: SIDE VIEW = INCHES, TOP VIEW = FEET
6
6
4
6
6
100.0
4.3
42.9
108.5
4.8
4.5
3.8
13.0
2

## Pump Calcs-1.25in
TDH Calculations for Selecting Pump
NOTES:
Assumes f = 0.022 for 1.25in pipe typical operating range
Static head in feet = measured or estimated
Friction head in feet = (fLv2)/(2gD) = (2.1355 x 10-5)LQ2 (Q in gpm, L in feet)
Pressure head in feet = 0.10524(Q/No. Pod)2 (Q in gpm) from orifice equations
Fill-in cells highlighted GREEN, if applicable.
BOX 1. SYSTEM INFO |  | 5 | 7 | 2.86 | 3.39 |  |  |  | BOX 2. FORCE MAIN AND FITTINGS
No. Pods | No. Nozzles per Pod | Nozzle PSI | hstat (feet) | Q (gpm) | L (feet) | hf (feet) | hp (feet) | TDH | PVC SCH 40 EQUIVALENT LENGTH ESTIMATE
1 | 4 | 7 | 10 | 13.56 | 95.1 | 0.37342 | 19.3509 | 29.7243 | Parameter | Feet | Number | Eq. Length
[9 empty] | Enter force main length→ | 25 | 1 | 25
BOX 3 - PROGRAMMABLE TIMER SETTINGS | [8 empty] | 90° elbow | 3.5 | 3 | 10.5
Design flow | [5 empty] | 600 | gpd |  | 45° elbow | 1.7 | 1 | 1.7
Drainback volume per dose to prevent freezing (no check valve) | [5 empty] | 0 | gal |  | Tee (diversion) | 7.6 | 1 | 7.6
Dosing interval | [5 empty] | 15 | min |  | Coupling | 2.3 | 1 | 2.3
Number of cycles (doses) | [5 empty] | 96 | d-1 |  | Check valve | 12 | 1 | 12
Drainback volume per day | [5 empty] | 0 | gpd |  | Ball valve (fully open) | 36 | 1 | 36
Pump total flow (5x design flow; 80% back; 20% forward; +drainback) | [5 empty] | 3000 | gpd |  | EQUIVALENT LENGTH TOTAL (FEET) | 95.1
Total volume per dose (all pods combined) | [5 empty] | 31.25 | gal
Net dose volume per pod (drainback not included) | [5 empty] | 31.25 | gal
Pump run time per cycle (if using minutes setting) | [5 empty] | 2.3046 | min
Pump run time per cycle (if using seconds setting) | [5 empty] | 138.2743 | sec
Pump off time per cycle | [5 empty] | 12.6954 | min
Nominal dosing tank volume (gal/in) | [5 empty] | 20 | gal in-1
Drawdown per dose* | [5 empty] | 1.5625 | in | *Prior to drainback
Loss through drainback hole while pump is active is assumed to be negligible
INSTRUCTIONS:
1. ENTER THE NUMBER OF PODS IN BOX 1.
2. ENTER THE NUMBER OF HELICAL SPRAY NOZZLES PER POD IN BOX 1.
3. SELECT 5 OR 7 PSI FROM PULLDOWN MENU IN BOX 1.
4. ENTER THE STATIC HEAD IN BOX 1.
5. ENTER THE FORCE MAIN LENGTH IN BOX 2.
6. ENTER THE NUMBER OF FITTINGS IN BOX 2.
7. WITH ALL ABOVE ENTERED - PLOT TDH FROM BOX 1. ON PUMP CURVE
8. ENTER ANTICIPATED FLOW IN BOX 3.
9. FOR SYSTEMS IN COLD CLIMATES, ENTER DRAINBACK FLOW IN BOX 3.
10. ENTER DOSING INTERVAL IN BOX 3.
11. ENTER DOSING TANK VOLUME (GAL/IN) BOX 3.
©2022 Anua
***ENTER PROJECT INFO HERE***

## Sloped Site Calcs
Distance to Finished Grade Calculation Sheet
Directions: Fill-in applicable cells in GREEN. Answers appear in BLUE. |  |  |  |  | ©2022 Anua
Design Inputs
DF | Design flow | 360 | gpd
H | Pod bury depth + pad height | 0.33 | ft
S | Slope | 3.7%
W | Pad width | 5 | ft
L | Pad length | 120 | ft
SAR | Soil application rate | 0.8 | gpd/ft2
Design Values
B | Infiltrative width required | 8.9189 | ft
D | Distance to surface | 3.9189 | ft
HLLF | Hydraulic loading per linear foot | 3 | gpd/ft
ID | Infiltrative distance | 3.75 | ft | 3.75

## Kaplan Calcs
Dispersal Field Water Mounding Calculation Sheet |  |  |  |  | Kaplan, 1991 Formulas1
R=√Q/πk' H=√Q2/2kk'
Directions: Fill-in applicable cells in GREEN. Answers appear in BLUE. |  |  |  | ©2020 Anua | 1Kaplan, O. Benjamin (1991). Septic Systems Handbook, 2nd Ed. Lewis Publishers, Inc. Chelsea, MI.
|  | Pad | Mounded Pad | Trench
| Design Inputs |  | Project Info |  | Conversion Table - Hydraulic Conductivity (K)2
Bedrooms, no. | 0 |  |  |  | m/d | cm/s | ft/d | gpd/ft2
Flow per bedroom | 0 | gpd |  |  | 1 | 0.00116 | 3.28 | 24.5
Effluent BOD5 loading | 10 | mg/l |  |  | 864 | 1 | 2830 | 21200
Pad, mounded pad or trench? | Pad |  |  |  | 0.305 | 0.000353 | 1 | 7.48
Pad, mounded pad or trench height, H | 6 | in |  |  | 0.041 | 4.73e-05 | 0.134 | 1
Pad, mounded pad or trench length, L | 0 | ft |  |  | 2USEPA (1993). Wellhead Protection: A Guide for Small Communities. EPA/625/R-93/002. USEPA. Washington, D.C.
Pad gravel, mounded pad sand or soil Ksat, k | Silt Loam | gpd/ft2
Soil Ksat, k' | Silty Clay | gpd/ft2
Soil application rate (SAR) | 0 | gpd/ft2
Minimum vertical separation (MVS) distance | 0 | in
Soil horizon 1 depth | 0 | in
Site slope % | 0%
| #DIV/0! |  | 8.4793 | 1.0599
Design Values
Total flow | 0 | gpd, or | 0 | ft3
Soil Ksat, k' | 0.14203 | ft/d
Basal radius, R | 0 | ft
Water mounding height, H | #DIV/0! | ft, or | #DIV/0! | in
Total MVS req'd | #DIV/0! | ft | #DIV/0! | in
Basal area, Ab | 0 | ft2
Pad, mounded pad or trench area per SAR | #DIV/0! | ft2
Pad, mounded pad or trench area, req'd | #DIV/0! | ft2
Pad, mounded pad or trench dimensions | #DIV/0! | ft W | 0 | ft L
Hydraulic loading per linear foot | #DIV/0! | gpd/ft
Absorptive area width (gpd/ft ÷ gpd/ft2) | #DIV/0! | ft
BOD5 dispersal field loading | #DIV/0! | lbs/d/ft2 | #DIV/0!
0.58884
Ksat Values | Rawls et al, 1998 |  | VA AOSS Regulations, 2011
| mm/h | gpd/ft2 | cm/d | gpd/ft2
Clay | 2 | 1.1777 | >17 | >4.17
Clay Loam | 4.2 | 2.4731
Fine Sand | 141.3 | 83.2031
Loam | 6.2 | 3.6508 | 10 to 17 | 2.45 to 4.17
Loamy Sand | 123 | 72.4273
Sand | 181.9 | 107.11
Sandy Clay | 0.9 | 0.52996 | 4 to <10 | 0.98 to <2.45
Sandy Clay Loam | 7.7 | 4.5341
Sandy Loam | 55.8 | 32.8573
Silt Loam | 14.4 | 8.4793 | <4 | <0.98
Silty Clay | 1.8 | 1.0599
Silty Clay Loam | 4.9 | 2.8853

## Allen Calcs
Dispersal Field Water Mounding Calculation Sheet
Directions: Fill-in applicable cells in GREEN. Answers appear in BLUE. |  |  |  |  | ©2020 Anua | Ksat Values | Rawls et al, 1998 |  | VA AOSS Regulations, 2011
[7 empty] | mm/h | gpd/ft2 | cm/d | gpd/ft2
|  | Design Inputs |  |  |  | Sand | 181.9 | 107.11 | >17 | >4.17
Q | Hydraulic loading | 0 | gpd | 0 | ft3/d | Fine Sand | 141.3 | 83.2031
l | Length | 0 | ft |  |  | Loamy Sand | 123 | 72.4273
W | Width | 0 | ft |  |  | Sandy Loam | 55.8 | 32.8573 | 10 to 17 | 2.45 to 4.17
K | Hydraulic conductivity (select soil texture) | Clay |  | 0.15781 | ft/d | Loam | 6.2 | 3.6508
SAR | Soil application rate | 0 | gpd/ft2 | 0 | ft/d | Silt Loam | 14.4 | 8.4793
D | Initial distance of saturation | 1 | ft |  |  | Sandy Clay Loam | 7.7 | 4.5341 | 4 to <10 | 0.98 to <2.45
[6 empty] | Clay Loam | 4.2 | 2.4731
|  | Design Values |  |  |  | Silty Clay Loam | 4.9 | 2.8853
R | Radius of drainfield | 0 | ft |  |  | Sandy Clay | 0.9 | 0.52996 | <4 | <0.98
A | Drainfield area | 0 | ft2 |  |  | Silty Clay | 1.8 | 1.0599
S | Water mound height above saturation depth | #DIV/0! | ft | #DIV/0! |  | Clay | 2 | 1.1777
L | Distance to lateral control (absorptive width) | #DIV/0! | ft
Allen, 1980 Formulas
Allen, D.H. (1980). Hydraulic Mounding of Groundwater Under Axisymmetric Recharge. Water Resource Research Center, University of New Hampshire. Durham, NH.

## Poeter Calcs
Dispersal Field Water Mounding Calculation Sheet
Directions: Fill-in applicable cells in GREEN. Answers appear in BLUE. |  |  |  | ©2020 Anua
|  | Design Inputs |  |  |  | Ksat Values | Rawls et al, 1998
Q | Volumetric (hydraulic) loading | 0 | gpd | 0 | m3/d |  | mm/h | gpd/ft2
L | Overall drainfield length | 0 | ft | 0 | m | Sand | 181.9 | 107.11
W | Overall drainfield width | 0 | ft | 0 | m | Fine Sand | 141.3 | 83.2031
K1 | Horizontal hydraulic conductivity, upper layer | Sandy Loam | gpd/ft2 | 1.3471 | m/d | Loamy Sand | 123 | 72.4273
K2 | Vertical hydraulic conductivity, lower layer | Silty Clay Loam | gpd/ft2 | 0.1183 | m/d | Sandy Loam | 55.8 | 32.8573
q' | Infiltration rate (if q' > K of upper layer, surfacing may occur) | #DIV/0! | gpd/ft2 | #DIV/0! | m/d | Loam | 6.2 | 3.6508
#DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | Silt Loam | 14.4 | 8.4793
|  | Design Values |  |  |  | Sandy Clay Loam | 7.7 | 4.5341
Hmax | Maximum water mound height | #DIV/0! | m |  |  | Clay Loam | 4.2 | 2.4731
|  | #DIV/0! | ft |  |  | Silty Clay Loam | 4.9 | 2.8853
Lext | Lateral extent of water mounding | #DIV/0! | m |  |  | Sandy Clay | 0.9 | 0.52996
|  | #DIV/0! | ft |  |  | Silty Clay | 1.8 | 1.0599
A | Drainfield area | 0 | ft2 |  |  | Clay | 2 | 1.1777
Poeter, et al., 2005 Formulas
Poeter, E., McCray, J., Thyne, G., and Siegrist, R. (2005). Designing Cluster and High-Density Wastewater Soil Absorption Systems to Control Groundwater Mounding. Small Flows Quarterly, Winter 2005, Vol. 6, No. 1, pp 36-48. Morgantown, WV.

## Flow per Panel Readings
Daily Flow Calculation per Panel Readings
Directions: Fill-in applicable cells in GREEN. Answers appear in BLUE. |  |  |  | ©2017 Anua
Project Info
Design Parameters | Daily design flow | 450 | gpd
| Design dose | 63 | gals per dose
| Days between visits | 75 | days
| Pump performance per drawdown | 57.3333 | gpm
Drawdown Information | Gallons per inch | 25
| Drainback volume | 22 | gallons
| Drawdown | 6 | in
| Elapsed time | 180 | sec | 3
| Pump performance | 57.3333 | gpm
| Total dose volume | 150
Elapsed Time Meter | Current reading | 95.46 | hr
| Previous reading | 23.56 | hr
| Elapsed time between visits | 4314 | min
| Pump performance | 57.3333 | gpm
| Days between visits | 75 | days
| System discharge | 3297.8133 | gpd
Elapsed Time Meter HH:MM:SS | Hours current reading | 0 | hr
| Hours previous reading | 0 | hr
| Minutes current reading | 0 | min
| Minutes previous reading | 0 | min
| Seconds current reading | 0 | sec
| Seconds previous reading | 0 | sec
| Total time between visits | 0 | min
| Pump Performance | 57.3333 | gpm
| System discharge | 0 | gpd
Cycle Counter | Cycle count current reading | 101612
| Cycle count previous reading | 99752
| Total cycles between visits | 1860
| System discharge | 3720 | gpd